## User Guidance
User Guidance
(Version 1.1 , 14/10/2014)
Welcome to the EFCTC F-gas recording tool!
Please read this guidance carefully as it will assist you in using the tool correctly
After reading this guidance, please proceed and fill out the User Identification sheet first.
The user identification sheet only needs to be completed once, and collects information of the user of the tool.
This tool uses colour codes to guide you through its use
Green boxes are free formats where you can enter the required information
Yellow boxes provide a selection option. You do not have to use the selection and can enter information as desired
Blue boxes contain formulaes, we recommend you do not change the formulaes, unless you are comfortable doing so
Warning: The use of macros needs to be enabled in the users' MS Excel® versions.
If you're not able to download the macros, download the version without macros.
We recommend that you keep a back-up blank copy of this tool, as well a back-up of each updated sheet
Installation page
The installation page contains two blocks:
The top box holds fixed data of the installation which usually does not change over time
This tool can keep records for a system with up to three circuits.
For each circuit you can indicate the refrigerant and the quantity charged.
IMPORTANT: If the charge size changes due to a modification, we recommend you start a new sheet
In the lower block, you can provide details on the activities performed on the system.
In case of charging of recovery, you should indicate which circuit has been serviced - use a numerical entry 1,2 or 3
In other cases, you do not have to enter the circuit number, e.g. you can enter "all"
The F-gas regulation requires that you should keep a record of the identity of the service engineer
In case of retrofitting, it will be necessary to create a new sheet.
If using a new mixed fluid, you can simulate the mixture with the GWP calculator.
Important Notice
This tool has been developed with care and is made available free of charge, we do not provide a helpdesk service
EFCTC decline all liability that may result from its use
The tool meets to the best of our knowledge the requirements for record keeping resulting from the F-gas regulation
In some countries, there may be additional requirements or a specific format may be needed
Please check with your local authority
The logbook has been designed to help ensuring compliance with Art. 6 (Record keeping) of the new F-Gas Regulation (EC) N°517/2014 and also: http://ec.europa.eu/clima/policies/f-gas/index_en.htm.
More copies can be downloaded via: http://www.fluorocarbons.org/logbook.
© Copyright
all rights reserved:
EFCTC/CEFIC

## User Identification
EFCTC F-Gas Regulation Containment Register
User Registration
Company Name
Street Address
Postal Address
City
Province
Postal Code
Country
This Company is
If Contractor please enter registration number
VAT number
Details of Principal Contact
Title
Initials
Name
Function
Tel#
Fax#
e-mail
Mailing address if different from company address
Street Address
Postal Address
City
Province
Postal Code
Country

## Installation page(s)
EFCTC F-Gas Regulation Recording tool
Installation
Name: | [7 empty] | In service since: | [6 empty] | Leak testing frequency
Address: | [7 empty] | Modification dates | [6 empty] | * Equipment containing > 5tes of CO2 equivalent (>10 tes for Hermetically sealed) but <50 tes of CO2 equivalent should leak test every 12 months or 24 months if a leakage detection system is installed
Place:
Country: | [14 empty] | * Equipment containing > 50 tes of CO2 equivalent but <500 tes of CO2 equivalent should leak test every 6 months or 12 months if a leakage detection system is installed
Manufacturer/ID/Registration nr: | [7 empty] | Status Active: | [6 empty] | * Equipment containing >500 tes of CO2 equivalent should leak test every 3 months or 6 months if a leakage detection system is installed
Equipment:
Circuit # | Fluid | GWP | Hermetic | Nominal Charge |  | System tonnes of CO2-eq. |  | Added kg | Recovered kg |  | Added - Recovered (excluding initial charge)
1 | Select | 0 |  |  | kg | 0 | tonnes | 0 | 0 |  | 0 | kg | 0 | tonnes CO2
2 | Select | 0 |  |  | kg | 0 | tonnes | 0 | 0 |  | 0 | kg | 0 | tonnes CO2
3 | Select | 0 |  |  | kg | 0 | tonnes | 0 | 0 |  | 0 | kg | 0 | tonnes CO2
*If the fluid is not in this list, use the GWP calculator!!!
Date dd/mm/yyyy | activity type |  | Circuit # | Fluid added kg |  |  |  | Fluid Recovered kg |  | inspection method |  |  | Direct: Type of sensor |  | sensitivity of sensor ppm | Name of Service Engineer | Registration number | Signature on file | Comments
(The destination of the recovered or reclaimed material need to be indicated here)

## GWPcalculator
GWP calculator
| GWP Calculator 1 |  |  |  | GWP Calculator 2 |  |  |  | GWP Calculator 3
MIX | Fluid | # % | GWP | MIX | Fluid | # % | GWP | MIX | Fluid | # % | GWP
| Select | 0% | 0 |  | Select | 0% | 0 |  | Select | 0% | 0
| Select | 0% | 0 |  | Select | 0% | 0 |  | Select | 0% | 0
| Select | 0% | 0 |  | Select | 0% | 0 |  | Select | 0% | 0
| Select | 0% | 0 |  | Select | 0% | 0 |  | Select | 0% | 0
| Select | 0% | 0 |  | Select | 0% | 0 |  | Select | 0% | 0
| Fluid name | ? 100% ? | GWP |  | Fluid name | ? 100% ? | GWP |  | Fluid name | ? 100% ? | GWP
| GWP calc. 1 | NOT 100% | NOT 100% |  | GWP calc. 2 | NOT 100% | NOT 100% |  | GWP calc. 3 | NOT 100% | NOT 100%

## Datasheet (hidden)
Datasheet EFCTC F-Gas Regulation Recording tool
Type | Nomenclature | Preference GWP 2 | Formula | CAS number | Common chemical name | Molecular Weight | GWP (SAR) | GWP (AR4) | GWP (AR5) | Preference GWP 1 | Preference GWP 2
| Select | 0
HCFC | R-21 | 148 | CHCl2F | 75-43-4 | Dichlorofluoromethane; R-21 | 103 |  |  | 148 | 148 | 148
HCFC | R-22 | 1810 | CHClF2 | 75-45-6 | Chlorodifluoromethane | 87 | 1500 | 1810 | 1760 | 1810 | 1810 | Activities | Detection | Circuit# | YESorNO | Function | Equipment
HFC | R-23 | 14800 | CHF3 | 75-46-7 | Trifluoromethane; Fluoroform; R-23 | 70 | 11700 | 14800 | 12400 | 14800 | 14800
HFC | R-32 | 675 | CH2F2 | 75-10-5 | Difluoromethane; R-32 | 52 | 650 | 675 | 677 | 675 | 675 | Commissioning | Portable Sensor | 1 | Yes | Contractor | stationary refrigeration equipment
HFC | R-41 | 92 | CH3F | 593-53-3 | Fluoromethane; R-41 | 34 |  | 92 | 116 | 92 | 92 | Inspection | Fixed Sensor | 2 | No | Owner | stationary air-conditioning equipment
HFC | R-43-10mee | 1640 | CF3-CF2-CHF-CHF-CF3 | 138495-42-8 | 1,1,1,2,2,3,4,5,5,5-Decafluoropentane | 252 | 1300 | 1640 | 1650 | 1640 | 1640 | Leak Detection | Pressure test (Nitrogen) | 3 |  | Operator | stationary heat pumps
CFC | R-113 | 6130 | CCl2F-CClF2 | 76-13-1 | 1,1,2-Trichlorotrifluoroethane; R-113 | 187 | 4800 | 6130 | 5820 | 6130 | 6130 | Service on circuit | Soap |  |  | Other, please specify | stationary fire protection equipment
CFC | R-114 | 10000 | CClF2-CClF2 | 76-14-2 | 1,2-Dichlorotetrafluoroethane; R-114 | 171 | 8040 | 10000 | 8590 | 10000 | 10000 | Leak Repair | Visual |  |  |  | refrigeration units of refrigerated trucks and trailers
CFC | R-115 | 7370 | CClF2-CF3 | 76-15-3 | Chloropentafluoroethane; R-115 | 155 | 5310 | 7370 | 7670 | 7370 | 7370 | Re-check after leak repair | Other, please specify |  |  |  | electrical switchgear
PFC | R-116 | 12200 | CF3-CF3 | 76-16-4 | Hexafluoroethane; R-116 | 138 |  | 12200 | 11100 | 12200 | 12200 | System modification | Not Applicable |  |  |  | organic Rankine cycles
HCFC | R-122 | 59 | CHCl2-CClF2 | 354-21-2 | 1,1,2-Trichloro-2,2-difluoroethane; R-122 | 169 |  |  | 59 | 59 | 59 | Recovery of Fluid
HCFC | R-122a | 258 | CHClF-CCl2F | 354-15-4 | 1,1,2-Trichloro-1,2-difluoroethane; R-122a | 169 |  |  | 258 | 258 | 258 | Retrofit
HCFC | R-123 | 77 | CHCl2-CF3 | 306-83-2 | 2,2-Dichloro-1,1,1-trifluoroethane; R-123 | 153 | 90 | 77 | 79 | 77 | 77 | Change of Lubricant
HCFC | R-123a | 370 | CHClF-CClF2 | 354-23-4 | 1,2-Dichloro-1,1,2-trifluoroethane; R-123a | 153 |  |  | 370 | 370 | 370 | Replacement of Compressor
HCFC | R-124 | 609 | CHClF-CF3 | 2837-89-0 | 2-Chloro-1,1,1,2-tetrafluoroethane; R-124 | 137 | 470 | 609 | 527 | 609 | 609 | Replacement of HX
HFC | R-125 | 3500 | CHF2-CF3 | 354-33-6 | Pentafluoroethane; R-125 | 120 | 2800 | 3500 | 3170 | 3500 | 3500 | Decommissioning
HCFC | R-132c | 338 | CCl2F-CH2F | 1842-05-3 | 1,1-Dichloro-1,2-difluoroethane; R-132c | 135 |  |  | 338 | 338 | 338 | Non-system intrusive
HFC | R-134 | 1100 | CHF2-CHF2 | 359-35-3 | 1,1,2,2-Tetrafluoroethane; R134 | 102 |  | 1100 | 1120 | 1100 | 1100 | Other, please enter activity
HFC | R-134a | 1430 | CH2F-CF3 | 811-97-2 | 1,1,1,2-Tetrafluoroethane; R-134a | 102 | 1300 | 1430 | 1300 | 1430 | 1430
HCC | R-140a | 160 | CCl3-CH3 | 71-55-6 | 1,1,1-Trichloroethane; Methyl chloroform; R-140a | 133 |  |  | 160 | 160 | 160
HCFC | R-141b | 725 | CCl2F-CH3 | 1717-00-6 | 1,1-Dichloro-1-fluoroethane; R-141b | 117 |  | 725 | 782 | 725 | 725
HCFC | R-142b | 2310 | CClF2-CH3 | 75-68-3 | 1-Chloro-1,1-difluoroethane; R-142b | 101 | 1800 | 2310 | 1980 | 2310 | 2310
HFC | R-143 | 353 | CHF2-CH2F | 430-66-0 | 1,1,2-Trifluoroethane; R-143 | 84 |  | 353 | 328 | 353 | 353
HFC | R-143a | 4470 | CF3-CH3 | 420-46-2 | 1,1,1-Trifluoroethane; R-143a | 84 | 3800 | 4470 | 4800 | 4470 | 4470
HCC | R-150 | 1 | CH2Cl-CH2Cl | 107-06-2 | 1,2-Dichloroethane; R-150 | 99 |  |  | 1 | 1 | 1
HFC | R-152 | 53 | CH2F-CH2F | 624-72-6 | 1,2-Difluoroethane; R-152 | 66 |  | 53 | 16 | 53 | 53
HFC | R-152a | 124 | CHF2-CH3 | 75-37-6 | 1,1-Difluoroethane; R-152a | 66 | 140 | 124 | 138 | 124 | 124
HFC | R-161 | 12 | CH2F-CH3 | 353-36-6 | Fluoroethane; R-161 | 48 |  | 12 | 4 | 12 | 12
HC | R-170 | 6 | CH3-CH3 | 74-84-0 | Ethane; R-170 | 30 |  | 6 |  | 6 | 6
PFC | R-218 | 8830 | CF3-CF2-CF3 | 76-19-7 | Octofluoropropane; Perfluoropropane; R-218 | 188 |  | 8830 | 8900 | 8830 | 8830
HCFC | R-225ca | 122 | CF3–CF2-CCl2H | 422-56-0 | 3,3-Dichloro-1,1,1,2,2-pentafluoropropane; R-225ca | 203 | 429 | 122 | 127 | 122 | 122
HCFC | R-225cb | 595 | CClF2-CF2-CClFH | 507-55-1 | 1,3-Dichloro-1,1,2,2,3-pentafluoropropane; R-225cb | 203 | 2030 | 595 | 525 | 595 | 595
HFC | R-227ea | 3220 | CF3-CHF-CF3 | 431-89-0 | 1,1,1,2,3,3,3-Heptafluoropropane; R-227ea | 170 | 2900 | 3220 | 3350 | 3220 | 3220
HFC | R-236cb | 1340 | CH2F–CF2-CF3 | 677-56-5 | 1,1,1,2,2,3-Hexafluoropropane; R-236cb | 152 |  | 1340 | 1210 | 1340 | 1340
HFC | R-236ea | 1370 | CF3-CHF-CHF2 | 431-63-0 | 1,1,1,2,3,3-Hexafluoropropane | 152 |  | 1370 | 1330 | 1370 | 1370
HFC | R-236fa | 9810 | CF3-CH2-CF3 | 690-39-1 | 1,1,1,3,3,3-Hexafluoropropane; R-236fa | 152 | 6300 | 9810 | 8060 | 9810 | 9810
HFC | R-245ca | 693 | CF2-CF2-CFH2 | 2730-64-5 | 1,1,2,2,3-Pentafluoropropane; R-345ca |  |  | 693 | 716 | 693 | 693
HFC | R-245cb | 4620 | CF3-CF2-CH3 | 1814-88-6 | Pentafluoropropane; R-245cb | 134 |  |  | 4620 | 4620 | 4620
HFC | R-245eb | 290 | CF3-CHF-CH2F | 431-31-2 | 1,1,1,2,3-Pentafluoropropane; R-245eb | 134 |  |  | 290 | 290 | 290
HFC | R-245fa | 1030 | CF3-CH2-CHF2 | 460-73-1 | 1,1,1,3,3-Pentafluoropropane; R-245fa | 134 |  | 1030 | 858 | 1030 | 1030
HFC | R-263fb | 76 | CF3-CH2-CH3 |  | 1,1,1-Trifluoropropane | 98 |  |  | 76 | 76 | 76
HFC | R-272ca | 144 | CH3-CF2-CH3 | 420-45-1 | 2,2-Difluoropropane | 80 |  |  | 144 | 144 | 144
| R-290 | 3 | CH3-CH2-CH3 |  | propane |  |  | 3 |  | 3 | 3
PFC | R-C318 | 10300 | -CF2-CF2-CF2-CF2- | 115-25-3 | Octafluorocyclobutane; Perfluorocyclobutane; R-318 | 200 | 8700 | 10300 | 9540 | 10300 | 10300
HFC | R-365mfc | 794 | CH3-CF2-CH2-CF3 | 406-58-6 | 1,1,1,3,3-Pentafluorobutane; R-365mfc | 148 |  | 794 | 804 | 794 | 794
HFC | R401A | 1182 | Blend |  | Calculated by GWP Calculator
HFC | R401B | 1288 | Blend |  | Calculated by GWP Calculator
HFC | R401C | 933 | Blend |  | Calculated by GWP Calculator
HFC | R402A | 2788 | Blend |  | Calculated by GWP Calculator
HFC | R402B | 2416 | Blend |  | Calculated by GWP Calculator
HFC | R403A | 3124 | Blend |  | Calculated by GWP Calculator
HFC | R403B | 4457 | Blend |  | Calculated by GWP Calculator
HFC | R404A | 3922 | Blend |  | Calculated by GWP Calculator
HFC | R405A | 950 | Blend |  | Calculated by GWP Calculator
HFC | R406A | 1943 | Blend |  | Calculated by GWP Calculator
HFC | R407A | 2107 | Blend |  | Calculated by GWP Calculator
HFC | R407B | 2804 | Blend |  | Calculated by GWP Calculator
HFC | R407C | 1774 | Blend |  | Calculated by GWP Calculator
HFC | R407D | 1627 | Blend |  | Calculated by GWP Calculator
HFC | R407E | 1552 | Blend |  | Calculated by GWP Calculator
HFC | R407F | 1825 | Blend |  | Calculated by GWP Calculator
HFC | R408A | 3152 | Blend |  | Calculated by GWP Calculator
HFC | R409A | 1585 | Blend |  | Calculated by GWP Calculator
HFC | R409B | 1560 | Blend |  | Calculated by GWP Calculator
HFC | R410A | 2088 | Blend |  | Calculated by GWP Calculator
HFC | R410B | 2229 | Blend |  | Calculated by GWP Calculator
HFC | R411A | 1597 | Blend |  | Calculated by GWP Calculator
HFC | R411B | 1705 | Blend |  | Calculated by GWP Calculator
HFC | R412A | 1709 | Blend |  | Calculated by GWP Calculator
HFC | R413A | 2053 | Blend |  | Calculated by GWP Calculator
HFC | R414A | 1478 | Blend |  | Calculated by GWP Calculator
HFC | R414B | 1362 | Blend |  | Calculated by GWP Calculator
HFC | R415A | 1507 | Blend |  | Calculated by GWP Calculator
HFC | R415B | 546 | Blend |  | Calculated by GWP Calculator
HFC | R416A | 1084 | Blend |  | Calculated by GWP Calculator
HFC | R417A | 2346 | Blend |  | Calculated by GWP Calculator
HFC | R417B | 2347 | Blend |  | Calculated by GWP Calculator
HFC | R417C | 1809 | Blend |  | Calculated by GWP Calculator
HFC | R418A | 1741 | Blend |  | Calculated by GWP Calculator
HFC | R419A | 2967 | Blend |  | Calculated by GWP Calculator
HFC | R419B | 2384 | Blend |  | Calculated by GWP Calculator
HFC | R420A | 1536 | Blend |  | Calculated by GWP Calculator
HFC | R421A | 2631 | Blend |  | Calculated by GWP Calculator
HFC | R421B | 3190 | Blend |  | Calculated by GWP Calculator
HFC | R422A | 3143 | Blend |  | Calculated by GWP Calculator
HFC | R422B | 2526 | Blend |  | Calculated by GWP Calculator
HFC | R422C | 3085 | Blend |  | Calculated by GWP Calculator
HFC | R422D | 2729 | Blend |  | Calculated by GWP Calculator
HFC | R422E | 2592 | Blend |  | Calculated by GWP Calculator
HFC | R423A | 2280 | Blend |  | Calculated by GWP Calculator
HFC | R424A | 2440 | Blend |  | Calculated by GWP Calculator
HFC | R425A | 1505 | Blend |  | Calculated by GWP Calculator
HFC | R426A | 1508 | Blend |  | Calculated by GWP Calculator
HFC | R427A | 2138 | Blend |  | Calculated by GWP Calculator
HFC | R428A | 3607 | Blend |  | Calculated by GWP Calculator
HFC | R429A | 17 | Blend |  | Calculated by GWP Calculator
HFC | R430A | 95 | Blend |  | Calculated by GWP Calculator
HFC | R431A | 38 | Blend |  | Calculated by GWP Calculator
HFC | R433A | 3 | Blend |  | Calculated by GWP Calculator
HFC | R433B | 3 | Blend |  | Calculated by GWP Calculator
HFC | R433C | 3 | Blend |  | Calculated by GWP Calculator
HFC | R434A | 3245 | Blend |  | Calculated by GWP Calculator
HFC | R435A | 30 | Blend |  | Calculated by GWP Calculator
HFC | R436A | 3 | Blend |  | Calculated by GWP Calculator
HFC | R436B | 3 | Blend |  | Calculated by GWP Calculator
HFC | R437A | 1805 | Blend |  | Calculated by GWP Calculator
HFC | R438A | 2265 | Blend |  | Calculated by GWP Calculator
HFC | R439A | 1983 | Blend |  | Calculated by GWP Calculator
HFC | R440A | 144 | Blend |  | Calculated by GWP Calculator
HFC | R441A | 3 | Blend |  | Calculated by GWP Calculator
HFC | R442A | 2800 | Blend |  | Calculated by GWP Calculator
HFC | R443A | 2 | Blend |  | Calculated by GWP Calculator
HFC | R444A | 93 | Blend |  | Calculated by GWP Calculator
HFC | R445A | 135 | Blend |  | Calculated by GWP Calculator
HFC | R502 | 4657 | Blend |  | Calculated by GWP Calculator
HFC | R504 | 4143 | Blend |  | Calculated by GWP Calculator
HFC | R507A | 3985 | Blend |  | Calculated by GWP Calculator
HFC | R508A | 13214 | Blend |  | Calculated by GWP Calculator
HFC | R508B | 13396 | Blend |  | Calculated by GWP Calculator
HFC | R509A | 5741 | Blend |  | Calculated by GWP Calculator
HFC | R511A | 9 | Blend |  | Calculated by GWP Calculator
HFC | R512A | 189 | Blend |  | Calculated by GWP Calculator
HC | R-600 | 4 | CH3-CH2-CH2-CH3 | 106-97-8 | butane |  |  | 4 |  | 4 | 4
HC | R-600a | 3 | CH(CH3)2CH3 | 75-28-5 | isobutane |  |  | 3 |  | 3 | 3
HC | R-601 | 5 | CH3CH2CH2CH2CH3 | 109-66-0 | pentane |  |  | 5 |  | 5 | 5
HC | R-601a | 5 | (CH3)2CHCH2CH3 | 78-78-4 | isopentane |  |  | 5 |  | 5 | 5
| R-610 | 4 | CH3CH2OCH2CH3 | 60-29-7 | ethoxyethane; diethyl ether |  |  | 4 |  | 4 | 4
| R-611 | 25 | HCOOCH3 | 107-31-3 | methyl formate |  |  | 25 |  | 25 | 25
| R-702 | 6 | H2 | 1333-74-0 | hydrogen |  |  | 6 |  | 6 | 6
| R-717 | 0 | NH3 | 7664-41-7 | ammonia |  |  | 0 |  | 0 | 0
| R-744 | 1 | CO2 | 124-38-9 | Carbon Dioxide |  | 1 | 1 | 1 | 1
HC | R-1150 | 4 | CH2=CH2 | 74-85-1 | Ethene; Ethylene | 28 |  | 4 |  | 4 | 4
HFO | R-1233zd | 4.5 | C3H2C1F3 |  |  |  |  | 4.5 |  | 4.5 | 4.5
HFO | R-1233xf | 1 | C3H2C1F3 |  |  |  |  | 1 |  | 1 | 1
HFO | R-1234yf | 4 | CF3-CF=CH2 | 754-12-1 | 2,3,3,3-Tetrafluoro-1-propene | 114 |  | 4 |  | 4 | 4
HFO | R-1234zeE | 7 | CF3-CH=CFH | 29118-24-9 1645-83-6 | (1E)-1,3,3,3-Tetrafluoro-1-propene | 114 |  | 7 | 1 | 7 | 7
| R-1270 | 2 | C3H6 |  | propylene |  |  | 2 |  | 2 | 2
HFC | R-1336mzz | 9 | CF3-CH=CH-CF3 | 407-60-3 | 1,1,1,4,4,4-hexafluoro-2-butene | 164 |  | 9 |  | 9 | 9
PFC | PFC-14 | 7390 | CF4 |  | tetrafluoromethane; Perfluoromethane, carbon tetrafluoride |  |  | 7390 |  | 7390 | 7390
PFC | R-31-10 (PFC-3-1-10) | 8860 | CF3-CF2-CF2-CF3 | 355-25-9 | Decafluorobutane; Perfluorobutane; R-3-1-10 | 238 | 7000 | 8860 |  | 8860 | 8860
PFC | R-41-12 (PFC 4-1-12) | 9160 | CF3-CF2-CF2-CF2-CF3 | 678-26-2 | Dodecafluoropentane; Perfluoropentane; R-4-1-12 | 288 | 6510 | 9160 |  | 9160 | 9160
PFC | R-51-14 (PFC 5-1-14) | 9300 | CF3-CF2-CF2-CF2-CF2-CF3 | 355-42-0 | Tetradecafluorohexane; Perfluorohexane; R-5-1-14 | 338 | 7400 | 9300 |  | 9300 | 9300
| GWP calc. 1 | NOT 100%
| GWP calc. 2 | NOT 100%
| GWP calc. 3 | NOT 100%